- ON 120VAC / 220VAC, 1 PHASE CONTROL CARDS,                           CHECK CONTROL CARD FOR PROPER VOLTAGE JUMPER SETTING.

PLEASE REFER TO PAGE 1 DIAGRAM FOR JUMPER LOCATION.

FOR 110VAC JUMPER PINS 2 AND 3.

FOR 220VAC JUMPER PINS 1 AND 2.

NOW  -  APPLY PROPER POWER TO ACTUATOR.

- DO NOT APPLY ANY ACTUATOR CONTROL SIGNAL AT THIS TIME.  DO NOT ATTACH CONTOL WIRING TO ACTUATOR IF NECESSARY.

- LED 3 SHOULD BE ON AND LED 4 THROUGH LED 9 SHOULD BE OFF.

- LED 1 OR LED 2 MAY BE ON.

- PRESS SET PB FOR 2 SECONDS.

- LED 9 SHOULD NOW BE ON AND THE CARD IS IN THE SETUP MODE.

- ACTUATOR OPEN SETUP PROCEDURE.

- PRESS UP PB AND HOLD UNTIL THE ACTUATOR GOES TO THE FULLY OPEN POSITION AND STOPS, THEN RELEASE UP PB.

- APPLY ACTUATOR OPEN CONTROL SIGNAL AT THIS TIME.

- PRESS MODE PB ONCE. THE OPEN SETTING IS NOW SAVED AND FINISHED.

- REMOVE THE OPEN CONTROL SIGNAL AT THIS TIME.  UNATTACH CONTOL WIRING TO ACTUATOR IF NECESSARY.

- ACTUATOR CLOSE SETUP PROCEDURE.

- PRESS DOWN PB AND HOLD UNTIL THE ACTUATOR GOES TO THE FULLY CLOSED POSITION AND STOPS, THEN RELEASE DOWN PB.

- APPLY ACTUATOR CLOSE CONTROL SIGNAL AT THIS TIME.

- PRESS MODE PB ONCE. THE CLOSE SETTING IS NOW SAVED AND FINISHED.

- AFTER FINISHING THE ABOVE SETUP PROCEDURE, PRESS THE SET PB ONCE AND THE ACTUATOR IS IN THE NORMANAL RUN MODE.

- CYCLE THE ACTUATOR FULLY OPEN AND CLOSED WITH CONTROL SIGINALS TO SEE IF IT RESPONDS PROPERLY.

- SETUP IS NOW COMPLETE.